## Tabelle1
Category | Name | Dim | Value | Dim_UBP | Value_UBP | Source Emissions | Confirmed 1 | description emissions | Dim_Cost | Cost | Source Cost | description cost | lifetime | Source LT
Conversion | Pellets | kgCO2-eq/kW | 51.2 | UBP/kW | 120 | KBOB 2016 | - |  | CHF/kW | 2110 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 20 | SIA 2032 (2020)
Conversion | Wood | kgCO2-eq/kW | 51.2 | UBP/kW | 120 | KBOB 2016 | - |  | CHF/kW | 2110 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 20 | SIA 2032 (2020)
Conversion | ASHP | kgCO2-eq/kW | 363.75 | UBP/kW | 682500 | KBOB 2016 | - |  | CHF/kW | 2290 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 20 | SIA 2032 (2020)
Conversion | GSHP | kgCO2-eq/kW | 896.5 | UBP/kW | 1296400 | KBOB 2016, http://www.erdsondenoptimierung.ch/index.php?id=269463 | - | including the borehole with the assumption of 0.04kW/m and 28.1kgCO2/m + 272.5 for the actual device | CHF/kW | 3970 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 33.9208 | SIA 2032 (2020)
Conversion | electric | kgCO2-eq/kW | 78 | UBP/kW | 145714.2857 | KBOB 2016, based on radiators with 0.07kW/m2 heating power | - |  | CHF/kW | 810 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 20 | SIA 2032 (2020)
Conversion | Natural Gas | kgCO2-eq/kW | 51.2 | UBP/kW | 120 | KBOB 2016 | - |  | CHF/kW | 1220 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 20 | SIA 2032 (2020)
Conversion | Oil | kgCO2-eq/kW | 51.2 | UBP/kW | 120 | KBOB 2016 | - |  | CHF/kW | 1040 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 20 | SIA 2032 (2020)
Conversion | district | kgCO2-eq/kW | 25.6 | UBP/kW | 60 | KBOB 2016, own estimation |  | overestimation, as there is only a "Übergabestation" and no burner, hence only half of the embodied emission of a burner(assumption) is counted | CHF/kW | 1550 | T. Gürber (2020), D. Sigrist (2018), WWF (2019), Energieschweiz und erneuerbarheizen (2020), energie 360° |  | 20 | SIA 2032 (2020)
PV | m-Si | kgCO2-eq/kWp | 2080 | UBP/kWp | 3170000 | KBOB 2016 | - |  | CHF/kW | THIS DATA IS INTERPOLATED | swissolar, BAPV |  | 30 | SIA 2032 (2020)
Distribution | hydronic heat distribution office | kgCO2-eq/m2 | 7.62 | UBP/m2 | 15000 | KBOB 2016 | - |  | CHF/m2 | 0 | included in floor heating /radiator | per EBF | 30 | SIA 2032 (2020)
Distribution | hydronic heat distribution residential | kgCO2-eq/m2 | 3.07 | UBP/m2 | 5480 | KBOB 2016 |  | I do not know why res and office are so different | CHF/m2 | 0 | included in floor heating /radiator | per EBF | 30 | SIA 2032 (2020)
Emission | floor heating | kgCO2-eq/m2 | 5.06 | UBP/m2 | 4040 | KBOB 2016 | - | per EBF | CHF/m2 | 150 | T. Gürber (2020) | per EBF, series of looped pipes connected to a warm water boiler. On https://comfortfloor.ch/lp/bodenheizung-kosten/, 180CHF/m2 is listed | 30 | SIA 2032 (2020)
Emission | radiator | kgCO2-eq/m2 | 5.46 | UBP/m2 | 10200 | KBOB 2016 |  | per EBF | CHF/m2 | 95.3333 | T. Gürber (2020) | per piece, wall-mounted radiator: 430 CHF. Assumption that per 15m2 one radiator is needed for demontage and montage, ca. 1000 per piece CHF https://www.ofri.ch/kosten/radiator-montieren | 30 | SIA 2032 (2020)
Emission | ceiling heating | kgCO2-eq/m2 | 5.77 | UBP/m2 | 39600 | KBOB 2016 |  | per EBF | CHF/m2 |  |  | per EBF | 30 | SIA 2032 (2020)
Distribution and Emission | air | kgCO2-eq/m2 | 1.7 | UBP/m2 | 2940 | KBOB 2016 |  | per EBF | CHF/m2 |  |  | per EBF | 30 | SIA 2032 (2020)
Ventilation | mechanical ventilation | (kgCO2-eq/m2)/(m3/hm2) | 5.8 | UBP/(m3/hm2) | 14480 | KBOB 2016 | - | according to linear interpolation, meaning (kgCO2 per EBF) per Aussenluftvolumenstrom, so multiply the number with the aussenluftvolumenstrom and then with EBF | CHF/m2 | 240 | T. Gürber (2020) | per EBF, comfort ventilation with heat recovery function | 30 | SIA 2032 (2020)
Ventilation | window ventilation | [5 empty] | - | [5 empty] | 30 | SIA 2032 (2020)
| None | kgCO2-eq/egal | 0 | UBP | 0 | None | - | Dummy for when a System "None" is chosen | CHF | 0 | None |  | 30 | egal